## Sheet1
Section,"Details"
Analysis of Consumption (2021-2023),"- Electricity: 3814.23 kWh
- Natural Gas: 19,711.67 kWh
#NAME?
- Comparison: Figures 5-1 and 5-2"
Calibration Criteria (ASHRAE Guideline 14-2014) [56],"- Monthly Data:
- NMBE: < 5%
- CV(RMSE): < 15%
- Hourly Data:
- NMBE: < 10%
- CV(RMSE): < 30%"
Understanding NMBE and CV(RMSE),"- NMBE: Signed error relative to the mean (percentage bias)
- Positive (NMBE > 0): Underestimation
- Negative (NMBE < 0): Overestimation
- CV(RMSE): Accuracy measure, percentage error of squared errors divided by actual mean"
Findings,"- Electricity:
- NMBE: −0.97%
- CV(RMSE): 12.90%
- Natural Gas:
- NMBE: 0.35%
- CV(RMSE): 14.50%"
Conclusion,"- Results within ASHRAE thresholds indicate strong correlation between actual and simulated consumption
- Calibration affirms reliability of energy simulations for informed energy management and retrofit decisions"